Building Model Parameters and its Calculation.

| Parameter | Value | How it is derived? | Why it is used? |
| --- | --- | --- | --- |
| H_ve | 62 W/K | Estimated ventilation/infiltration loss for a refurbished 1968 MFH. | Represents ventilation heat loss. |
| H_tr | 185 W/K | Estimated from improved envelope transmission losses after refurbishment. | Represents reduced heat loss through walls, roof, and floor. |
| H_tr_light | 36.0 W/K | Estimated from the lighter envelope parts, mainly upgraded windows. | Used if the model separates transparent/light thermal paths. |
| c_bldg | 35 Wh/(m²K) | Chosen as a medium thermal mass typical for a 1960s masonry building. | Controls how quickly indoor temperature changes. |
| area_floor | 287.92 m² | Taken directly from the building document. | Required size input for the model. |
| height_room | 2.5 m | Typical heated room height for a multi-family house. | Needed to estimate indoor air volume. |
| T_offset | -2 K | Chosen as a lower heating-curve offset for the better-insulated EnEV case. | Better insulation means lower supply-temperature needs. |
| T_amb_lim | 20 °C | Standard control threshold for heating operation. | Common comfort-based heating limit. |
| mdot_hp | 0.27 | Chosen as a plausible hydronic mass-flow value for the system. | Needed for heating-system calculations. |
| w_east.area | 12.0 m² | Estimated east-facing window area. | Window area affects transmission loss if windows are included. |
| w_east.tilt | 90° | Vertical façade window. | Standard façade geometry. |
| w_east.azimuth | 90° | East-facing orientation. | Needed only if window orientation is used in the model. |
| w_east.c_frame | 0.3 | Assumed frame fraction. | Reduces effective transparent area. |
| w_south.area | 18.0 m² | Estimated south-facing window area. | South windows often represent a major façade area. |
| w_south.tilt | 90° | Vertical façade window. | Standard façade geometry. |
| w_south.azimuth | 180° | South-facing orientation. | Needed only if orientation is used. |
| w_south.c_frame | 0.3 | Assumed frame fraction. | Reduces effective transparent area. |
| w_west.area | 12.0 m² | Estimated west-facing window area. | West windows affect envelope heat loss. |
| w_west.tilt | 90° | Vertical façade window. | Standard façade geometry. |
| w_west.azimuth | 270° | West-facing orientation. | Needed only if orientation is used. |
| w_west.c_frame | 0.3 | Assumed frame fraction. | Reduces effective transparent area. |
| w_north.area | 9.0 m² | Estimated north-facing window area. | North windows mostly influence heat loss. |
| w_north.tilt | 90° | Vertical façade window. | Standard façade geometry. |
| w_north.azimuth | 0° | North-facing orientation. | Needed only if orientation is used. |
| w_north.c_frame | 0.3 | Assumed frame fraction. | Reduces effective transparent area. |
| position.lat | 52.44 | Approximate latitude of the site in Germany. | Needed for weather/climate inputs. |
| position.long | 9.74 | Approximate longitude of the site. | Needed for geographic simulation inputs. |
| position.altitude | 55 m | Approximate altitude of the site. | Useful for weather calculations. |
| position.timezone | Europe/Berlin | Timezone consistent with the building location. | Needed for time-series alignment. |

Parameter and its calculation

For building model, the main parameters are:

- H_ve for ventilation heat loss.

- H_tr for envelope transmission loss.

- H_tr_light only if the model still separates light parts like windows.

- c_bldg for thermal mass.

- area_floor for building size.

- height_room for air volume.

- T_offset, T_amb_lim, and mdot_hp for heating-system behavior.

- Window area for transmission losses

Assumptions used:

- Floor area Afloor = 287.92 m2

- Indoor temperature Tin​=20∘C

- Outdoor temperature Tamb​=0∘C

- Heating load reference = 10.968 kW (from document)

- Older German MFH archetype values for the missing thermal data from TABULA webtool.

- Ventilation heat loss H_ve

This is the ventilation heat-loss coefficient, and it is usually estimated from air exchange rate and room volume.

A common approximation is:

Hve​=0.34⋅n⋅V

where:

- 0.34 is the air heat-capacity factor in Wh/(m3K),

- n is air change rate in 1/h,

- V is heated volume in m3.

Using building data:

V=Afloor​ x height_room = 287.92 x 2.5 = 719.8m3

If we choose a refurbished-air-change rate of:

n=0.253h−1

then:

Hve ​= 0.34 x 0.253 x 719.8 = 61.9W/K ≈ 62W/K

Hve​ = 62W/K

- Transmission heat loss H_tr

This is the transmission heat-loss coefficient through the envelope.

In simplified building models, total transmission is often split into a few envelope parts and choose EnEV-style U-values.

- heavy opaque parts: walls, roof, floor

- light transparent parts: windows.

The general formula is:

Htr ​= ∑(Ui​Ai​)

Set of assumptions:

- External walls: A =150m2, U=0.28

- Roof: A=120m2, U=0.20

- Floor/slab: A=120m2, U=0.25

Then:

Htr,opaque​ = 150 x 0.28 + 120 x 0.20 + 120 x 0.25

Htr,opaque​ = 42 + 24 + 30 = 96W/K

Htr,opaque​ = 96W/K + 89 W/K

Here,

89 W/K is consistent with windows and other light components in a refurbished MFH if the total glazed area is moderate and the window U-value is still above modern standards.

So,

Htr,opaque​ = 185W/K

Now add the light parts, mainly windows, separately as H_tr_light.

- Light transmission H_tr_light

This is the transmission coefficient for the lighter, faster components, mainly windows.

This is usually the window part:

Htr,light ​= ∑(Uwin​Awin​)

Suppose the total window area remains:

Awin ​= 12 + 18 + 12 + 9 = 51m2

For EnEV-refurbished windows, a reasonable U-value is around:

Uwin​=0.70W/(m2K)

Then:

Htr,light ​= 0.70 x 51 = 35.7W/K ≈ 36W/K

Htr,light ​= 36W/K

- Specific thermal capacity c_bldg

This is the building thermal capacity per square meter.

This value is not usually computed from geometry alone. It is estimated from thermal mass:

cbldg​ =Afloor​Cbuilding​​

where:

Cbuilding​ = total thermal capacitance

If we assume the building stores about 10,000Wh/K

then:

cbldg​ =10000 Wh/K​287.92​​

cbldg​ ​ ≈ 34.7Wh/(m2K) = 35Wh/(m2K)

- height_room

This helps estimate indoor air volume and thermal mass.

The building data provides building height, but not average heated-room height, so we assumed a typical room height.

height_room = 2.5m

- T_offset

It is a control/heating-curve setting.

Based on the idea that older buildings generally need a warmer supply temperature than better-insulated buildings.

T_offset = -2 K

- T_amb_lim

This is a control threshold which tells controller when heating is necessary.

Common comfort-based heating limit:

T_amb = 20°C

- mdot_hp

This is the heat-pump water mass-flow estimate.

It is a modeling assumption used for the heating-system.

mdot_hp = 0.27

- Window areas

Based on building type and age, we estimated the window area and location from TABULA webtool.

Different state of building model

- Original state: highest losses.

- EnEV: improved insulation and lower losses.

- KfW: best efficiency and lowest losses.

| Parameter | Original | EnEV | KfW |
| --- | --- | --- | --- |
| name | mfh_1968_0_soc | mfh_1968_1_enev | mfh_1968_2_kfw |
| H_ve | 72 W/K | 62 W/K | 54 W/K |
| H_tr | 310 W/K | 185 W/K | 118 W/K |
| H_tr_light | 58.0 W/K | 36.0 W/K | 24.0 W/K |
| c_bldg | 35 Wh/(m²K) | 35 Wh/(m²K) | 35 Wh/(m²K) |
| area_floor | 287.92 m² | 287.92 m² | 287.92 m² |
| height_room | 2.5 m | 2.5 m | 2.5 m |
| T_offset | 10 K | -2 K | -7 K |
| T_amb_lim | 20 °C | 20 °C | 20 °C |
| mdot_hp | 0.30 | 0.27 | 0.24 |

Shared geometry

The window geometry and location stay the same in all three versions:

- east: 12.0 m², 90°, frame factor 0.3

- south: 18.0 m², 180°, frame factor 0.3

- west: 12.0 m², 270°, frame factor 0.3

- north: 9.0 m², 0°, frame factor 0.3

- location: 52.44, 9.74, 55 m, Europe/Berlin