Model Predictive Control

1. System model (all formulas, shared with RL)
2. MPC Model formula


1. System model

This is the shared physical model of the heat pump and hot water tank. It is the same environment that can be used by RL controllers like PPO.
The system model is the discrete-time dynamics that map from current state and input to the next state.

  - Main variables

Time and control variables
- k: discrete time step. (step 0, 1, 2, …).

- Δt: sampling time, time length of 1 step, e.g. 15 minutes = 0.25h.
- H: MPC prediction horizon, for example 16 steps.
- Pel(k): electrical power of the heat pump in kW at step k.
- Pmax​: maximum electrical power [kW].

- Pel(k−1): previous power value used for switching penalty.

Thermal variables

- Tamb(k): ambient temperature [°C].

- Ttank(k): hot water tank temperature [°C].

- Tmin​: minimum tank temperature [°C].

- Tmax​: maximum tank temperature [°C].

- SOC(k): storage state of charge, from 0 to 1.

- Etank(k): stored thermal energy in tank [kWh].

- Emax​: usable tank energy capacity [kWh]

Flow variables

- m(k): mass flow rate [kg/s].

- V(k): volumetric flow rate [m³/s].

- ρ: water density [kg/m³].

- cp​: specific heat capacity of water [J/ (kg· K)].

- ΔT: supply-return temperature drop [°C], often assumed 5°C.

- Qsh(k): heating demand energy or heat transfer quantity.

Exogenous inputs

- d(k): building heat demand [kW].

- p(k): electricity price [€/kWh].

- forecasts of Tamb, p, and demand over the horizon

The controller output is only Pel(k), while all other quantities are either state variables or external inputs.

1.2 Heat pump COP

The real manufacturer data(aroTHERM) confirms that COP depends strongly on ambient temperature and flow temperature.

Why COP depends on temperatures

Real manufacturers show COP depends on:

- Heat source temperature (outside air, ground, etc.).

- Heat sink temperature (flow / tank temperature).

Physically:

- If outside air is warmer, the pump can “lift” heat more easily → COP higher.

- If flow/tank temperature must be very high, the pump must work harder → COP lower.

Practical model is:

COP(k) = a + bTamb(k) − c (Ttank(k)−Tref)

where:

- Tamb(k): outdoor air temperature (from weather API)

- Ttank(k): tank / flow temperature (from state)

- Tref​: reference temp (e.g. 45°C)

- a, b, c: coefficients calibrated using manufacturer data (e.g. Vaillant tables)

is a simple linear approximation of the 2-D table that manufacturer provides (COP as function of source and sink temperature).

- a: base COP at reference conditions.

- bTamb(k): more COP when outside is warmer.

- −c(Ttank−Tref): less COP when tank hotter than reference.

This kind of affine model is commonly used because:

- It is easy to fit by linear regression to manufacturer COP tables. (Vaillant Table)

- It is smooth and convex enough for many MPC solvers.

So, the form is not “physically exact”, but it is a reasonable engineering approximation

Keep it to a realistic range:

COPeff(k) = min (max (COP(k), COPmin), COPmax)

Reason:

- The linear model could give nonsense like COP = 0 or COP = 10 in extreme conditions.

- Real heat pumps usually have COP in some range, e.g. 2–5 for space heating.

So, we clip to a realistic interval to keep the state equations and optimization stable.

1.3 Heat delivered by the heat pump:

The heat pump converts electricity into useful heat:

Qin(k) = COPeff(k) Pel(k)

This is directly derived from the definition of COP:

COP = heat outputelectric power input

So, if COP is 3.5 and the electric input is 2 kW, the thermal output is 7 kW.

It tells the tank how much heat it receives from the heat pump.

1.4 Tank energy balance

The hot water tank stores energy and loses energy when the building draws heat or when heat leaks to the surroundings.

This is conservation of energy over one time step.

Continuous-time idea

In continuous time, a generic energy balance is

dEtankdt = heat in − heat out

This form is standard in thermodynamics and used to derive dynamic models of thermal systems.

For the tank:

- Heat in: Qin(t) (from heat pump),

- Heat out: building demand d(t), plus tank losses Qloss(t).

So:

dEtankdt = Qin(t) − d(t) − Qloss(t)

Discrete-time approximation

Approximate the derivative with forward Euler:

dEtankdt ≈  Etankk+1 - Etank(k)Δt

Plug this into the continuous equation:

Etankk+1 - Etank(k)Δt = Qin(k) − d(k) − Qloss(k)

Now multiply both sides by Δt:

Etank(k+1) − Etank(k) = (Qin(k) − d(k) − Qloss(k)) Δt

Rearrange to get:

The discrete-time energy conversation:

Etank(k+1) = Etank(k) + (Qin(k) − d(k) − Qloss(k)) Δt

where:

- Etank(k) is stored thermal energy,

- d(k) is the building demand,

- Qloss(k) is tank heat loss,

- Δt is the time step in hours.

Interpretation:

- If more heat comes in than goes out, Etank​ increases.

- If more leaves (demand + losses) than comes in, Etank​ decreases.

This equation is just conservation of energy:

- what comes in increases storage,

- what the building uses decreases storage,

- what leaks out also decreases storage.

1.5 Tank losses

Tank heat losses:

Qloss(k)=kloss max (Ttank(k)−Tamb(k),0)

This is a simplified “Newton’s law of cooling”:

- Heat loss rate is proportional to temperature difference between object and environment.

- If tank is cooler than ambient, you set losses to zero because you ignore reverse heat gain.

So:

- If Ttank ≫ Tamb: big positive difference → large loss.

- If Ttank ≤ Tamb: you clamp to zero to avoid unphysical “negative loss”.

More detailed tank models include stratification layers and more complex loss distributions, but at high level the proportional loss model is standard for building energy simulations.

For MPC, linear or piecewise linear loss keeps the model simple and solvable.

This means:

- if tank temperature is much higher than ambient, losses are larger,

- if tank is not hotter than ambient, the loss term is set to zero.

This is a standard first-order thermal loss approximation. It keeps the model simple while still reflecting the main physics.

1.6 SOC of the tank

SOC as the internal storage state.

A linear mapping is:

SOC(k) = Etank(k)/Emax

- Etank​(k): energy stored in tank [kWh]

- Emax​: usable tank capacity [kWh]

If:

- Etank = 0 → SOC = 0.

- Etank = Emax → SOC = 1.

Why linear relation to temperature is okay

Physical relation:

Etank = Ctank⋅ (Ttank − Tref)

where Ctank​ is heat capacity (mass × specific heat).
Between two limits Tmin​ and Tmax​, this becomes an affine mapping, so SOC is linearly related to temperature as long as Ctank is roughly constant.

Choose:

- Ttank = Tmin​ when SOC = 0.

- Ttank = Tmax​ when SOC = 1.

So, the linear interpolation is consistent and easy.

and the inverse relation for temperature is:

Ttank​(k) = Tmin ​+ SOC(k)(Tmax​−Tmin​)

This is practical because the hot water tank is treated as one lumped thermal storage node.

1.7 Heat demand

d(k) is just “how much heat the building wants now” at step k.

The MPC will receive demand forecast over the horizon:

dfore(i), i = k, …, k+H−1

This can come from:

- real building data,

- a demand forecast model,

- or synthetic profiles during testing.

The formula itself is just a symbol; the important part is that it enters the energy balance as an outflow.

1.9 Constraints

Control constraints:

0 ≤ Pel(i) ≤ Pmax

Can enforce SOC hard bounds (never go below 0 or above 1) by clipping in the dynamics.

0 ≤ SOC(i) ≤ 1

Simple single-node energy balance:

  - Tank temperature from SOC:

Ttank(k) = Tmin + SOC(k)⋅(Tmax−Tmin)

- Losses to ambient:

Qloss(k) = kloss⋅max (Ttank(k)−Tamb(k),0)

- HP heat input:

Qin(k) = COPeff(k)⋅Pel(k)

- Energy balance in the tank:

Etank(k+1) = Etank(k) + (Qin(k) − d(k) − Qloss(k)) ⋅Δt

- Update SOC and clip:

SOC(k+1) = clip (SOC(k) + (Qin(k)-d(k)- Qloss(k)) ⋅Δt Emax, 0, 1)

  - MPC Model Formula

Now we build the actual optimization problem. This is the part of controller where it solves every time step.

2.0 Decision variable

The MPC decides the future sequence:

u = [Pel(k), Pel(k+1), …, Pel(k+H−1)]

where H is the prediction horizon. A typical value is 12–16 steps, which means 3–4 hours if Δt =15minutes.

The controller only applies the first action, then re-solves at the next step. That is the standard receding-horizon idea of MPC.

2.1 Electricity cost

Per-step electricity cost:

Jelec(k) = p(k) Pel(k) Δt

- p(k) is energy price [€/kWh] from API.

- Pel(k) is power [kW].

- Multiply power by time [h] to get energy [kWh].

- Then multiply energy by price per kWh to get cost [€]

Over prediction horizon:

Jelec= i=kk+H-1p(i) Pel(i) Δt

This is the main term in the MPC objective.

2.2 Switching cycle:

We want to limit fast on/off or large power jumps. To avoid compressor short-cycling,

ΔP(i) = Pel(i) − Pel(i−1)

We can implement by:

Jswitch(i) = wswitch⋅(Pel(i)-Pel(i-1))2

2.3 Total MPC cost:

The objective over the horizon is:

J = i=kk+H-1[p(i) Pel(i) Δt + wswitch Peli-Peli-12]

The optimization problem is:

min{Pel(i)}k +H -1i=k J

subject to:

- the tank dynamics,

- the COP model,

- 0 ≤ Pel(i) ≤ Pmax

This is the standard MPC formulation.